## Sheet1
필요 Data Element
Name | Type | HES Unit | Unit | Scale Factor | Description
Device | uint16 | 1 | N/A | 0 | This register value represents the type of device. 0x0000: Unknown
ProVer | uint16 | 0.01 | N/A | -2 | This register represents the latest version of the protocol.
MinorVer | uint16 | 0.01 | N/A | -2 | This register represents the software version under this model. If the value of this register is 0xAABB, then AA represents the low byte of the software version of the DSP, and BB represents the low byte of the software version of the LCD. Remark: The register “MinorVer”is associated with the register” MajorVer”.
SN | uint64 | BCD | N/A | 0 | The values of these four registers represent the serial number of the machine. Remark: Serial number is composed of 16 characters(8 bytes)，the most significant 3 characters is not used, only used the left 13 characters. 7 / 50 Such as 0x0001010091114001, it represents the inverter serial number is 1010091114001
model | String20 | 1 | N/A | 0 | These 10 registers represent the model of the device. The value of the register is a character type, e.g. SCH125KTL-DO/US-600
Tyield | uint32 | 1kWh | kWh | 0 | Total energy to grid eg.0X01562318=22422296kWh, Register (addr 0X0016)=High 16 bit (data 0X0156) Register (addr 0X0017)=Low 16 bit (data 0X2318)
Dyield | uint16 | 0.1kWh | Kwh | -1 | The accumulated kWh of that day
PF | int16 | 0.001 | N/A | -3 | Power factor
Pmax | uint16 | 0.1KW | kW | -1 | AC maximum active power of that day
Pac | uint16 | 0.1KW | kW | -1 | AC active power
Sac | uint16 | 0.1kVA | kVA | -1 | AC Apparent power
Uab | uint16 | 0.1V | V | -1 | Grid voltage Uab
Ubc | uint16 | 0.1V | V | -1 | Grid voltage Ubc
Uca | uint16 | 0.1V | V | -1 | Grid voltage Uca
Ia | uint16 | 0.1A | A | -1 | Grid A phase current
Ib | uint16 | 0.1A | A | -1 | Grid B phase current
Ic | uint16 | 0.1A | A | -1 | Grid C phase current
Freq | uint16 | 0.1Hz | Hz | -1 | Grid frequency
Tmod | int16 | 0.1C | C | -1 | Heatsink temperature
Tamb | int16 | 0.1C | C | -1 | Ambient temperature
Mode | uint16 | N/A | N/A | 0 | 0x8000: Fault 0x4000: Check 0x2000: Standby 0x1000: Running 0x0800: Derate
Time | uint64 | N/A | N/A | 0 | Error timestamp(yyyy-mm-dd-hh-mm-ss-N/A) ,eg.0X2012071615181000=2012-7-16 15:18:10
Qac | int16 | 0.1kva | kvva | -1 | AC current reactive power
BusCapacitance | int16 | 1uF | uF | 0 | Bus capacitance
AcCapacitance | int16 | 1uF | uF | 0 | AC capacitance
Pdc | uint16 | 0.1kW | kW |  | PV input total power
PmaxLim | uint16 | 1Kw | kW |  | Maximum active power
SmaxLim | uint16 | 1kVA | kVA |  | Maximum apparent power
전송데이터 형식샘플(Json)
{ "Device": "IoT_002", "Time": "2024-11-12 15:18:10", "ProVer": 12345, "MinorVer": 12345, "SN": 123456789012345, "model": "mo-2093", "Status": { "Tyield": 4929.23, "Dyield": 432.77, "PF": 23.81, "Pmax": 12345, "Pac": 12345, "Sac": 12345, "Uab": 12345, "Ubc": 12345, "Uca": 12345, "Ia": 12345, "Ib": 12345, "Ic": 12345, "Freq": 12345, "Tmod": 32.8, "Tamb": 27.4, "Mode": "Running", "Qac": 1189, "BusCapacitance": 16.2, "AcCapacitance": 17.1, "Pdc": 42.12, "PmaxLim": 46.82, "SmaxLim": 39.92 } }